## Resumen Ejecutivo
GPW — Facility Build-Out CAPEX Analysis (v2 — Revised)
Shell industrial ~5,000 m² (53,820 sq ft) — Monterrey, NL — March 2026
KEY ASSUMPTIONS
Facility size | 5,000 m² (53,820 sq ft) | Shell with loading docks, transformer 500kVA included
Production area (est.) | ~3,000 m² (32,290 sq ft) | Celdas, burn-in, kitting, staging
Office/support area (est.) | ~800 m² (8,611 sq ft) | Engineering, quality, admin, meeting rooms
Warehouse/staging (est.) | ~1,200 m² (12,917 sq ft) | Raw material, WIP, finished goods
Electrical demand | ~250-350 kW peak | Burn-in 156 kW + HVAC + lighting + equipment
Existing infrastructure | Transformer 500kVA + CFE hookup + loading docks | Already in shell — no need to budget
FX Rate | 17.8167 MXN/USD | Per financial model (Presupuesto Anual)
Production cells | 22 cells (3 Kit + 12 Box + 2 Smoke + 3 Assy + 2 BI) | Per Factory Cost file
Security note | Private industrial park — no CCTV/perimeter in Phase 1 | Will add from operating cash flow later
Category / Line Item | Low (USD) | Mid (USD) | High (USD) | Best Est. (USD) | Notes / Source
1. ELECTRICAL INFRASTRUCTURE
Tableros de distribución principal + secundarios | 12000 | 18000 | 25000 | 18000 | Main switchgear + branch panels for production zones. $10K in Factory Cost covers burn-in only — need plant-wide.
Distribución eléctrica interior (cableado, canalizaciones) | 25000 | 40000 | 55000 | 40000 | Charola tipo malla + conduit para 5,000 m². ~$8/m² mid estimate.
Iluminación industrial LED | 18000 | 28000 | 40000 | 28000 | ~200 luminarias LED high-bay 200W. $5.2/sq ft mid. Source: Industrial construction cost guides 2025.
Sistema de tierras físicas + pararrayos | 5000 | 8000 | 12000 | 8000 | Malla de tierras perimetral + varillas + pararrayos. Crítico para ESD y equipo electrónico.
Planta de emergencia (200 kW) | INCLUDED | INCLUDED | INCLUDED | INCLUDED | YA INCLUIDO en Factory Cost: generador $30K (shared) en Burn-In sheet.
UPS modular (156 kW) | INCLUDED | INCLUDED | INCLUDED | INCLUDED | YA INCLUIDO en Factory Cost: UPS $75K (shared) en Burn-In sheet.
Subtotal | 60000 | 94000 | 132000 | 94000
2. HVAC & COOLING
HVAC producción — paquetes rooftop (3,000 m²) | 60000 | 85000 | 120000 | 85000 | ~25 TR para área de producción. 3-4 unidades rooftop 7.5 TR. $17-22/m². Source: HVAC industrial MX.
HVAC oficinas (800 m²) | 15000 | 22000 | 30000 | 22000 | Mini-splits o paquetes, ~6 TR total.
Chiller plant (burn-in) — instalación completa | 25000 | 40000 | 55000 | 40000 | Factory Cost has chiller at $30K equip only. Installation, piping, pumps add $25-55K.
Ductería y distribución de aire | 15000 | 25000 | 35000 | 25000 | Ductwork, diffusers, returns for full plant. ~$5/m² mid.
Subtotal | 115000 | 172000 | 240000 | 172000
3. FLOORING
Piso epóxico antiestático — producción (3,000 m²) | 45000 | 75000 | 105000 | 75000 | ESD-rated epoxy $15-35/m². CRITICAL for server assembly. Source: Epoxy flooring cost guides 2025.
Piso epóxico estándar — warehouse (1,200 m²) | 12000 | 21000 | 30000 | 21000 | Standard industrial epoxy $10-25/m². For forklift traffic and cleanliness.
Nivelación / reparación de piso base | 8000 | 15000 | 22000 | 15000 | Shell floors often need grinding/leveling before epoxy. $3-4.5/m² for 4,200 m².
Subtotal | 65000 | 111000 | 157000 | 111000
4. OFFICE BUILD-OUT & SUPPORT AREAS
Construcción de oficinas (800 m² — tablaroca, puertas, acabados) | 40000 | 60000 | 80000 | 60000 | Drywall partitions, doors, finishes, restrooms. ~$75/m² mid. Source: MX commercial build-out.
Sala de capacitación / training room | 5000 | 8000 | 12000 | 8000 | Whiteboard, projector, tables, AC — multi-purpose.
Laboratorio de calidad / incoming inspection | 8000 | 15000 | 22000 | 15000 | Benches, lighting, basic metrology area.
Comedor / break room | 5000 | 10000 | 15000 | 10000 | Kitchen equipment, tables, ventilation. NOM-001-STPS requirement.
Vestidores y sanitarios adicionales | 8000 | 12000 | 18000 | 12000 | Lockers, showers (optional), additional restrooms for 74 HC.
Cuarto de MES/IT/servidores | 5000 | 10000 | 15000 | 10000 | Small server closet, AC, UPS, patch panels.
Subtotal | 71000 | 115000 | 162000 | 115000
5. IT & DATA INFRASTRUCTURE
Cableado estructurado Cat6A (100+ puntos) | 15000 | 25000 | 35000 | 25000 | ~100-120 drops @ $200-300 USD/drop installed+certified.
Red Wi-Fi industrial (APs + controlador) | 5000 | 8000 | 12000 | 8000 | 10-15 industrial-grade APs for 5,000 m². Ubiquiti/Aruba.
Core switch + distribution switches | 5000 | 8000 | 12000 | 8000 | Layer 3 core + edge switches for MES, test, office VLANs.
Enlace de internet dedicado + respaldo | 3000 | 5000 | 8000 | 5000 | Fibra dedicada + enlace de respaldo. Setup + first month.
Subtotal | 28000 | 46000 | 67000 | 46000
6. FIRE PROTECTION & SAFETY
Sistema de sprinklers (5,000 m²) | 40000 | 65000 | 90000 | 65000 | Wet pipe sprinkler per NFPA 13. $120-300 MXN/m². Source: Protectamx.com 2024.
Detección de humo / alarma centralizada | 8000 | 12000 | 18000 | 12000 | Addressable fire alarm panel + detectors. Full plant coverage.
FM-200 / agente limpio — burn-in rooms | INCLUDED | INCLUDED | INCLUDED | INCLUDED | YA INCLUIDO en Factory Cost: $15K per cell en Burn-In sheet.
Extintores, señalización, rutas de evacuación | 3000 | 5000 | 8000 | 5000 | Per NOM-002-STPS-2010. Extinguishers + signage + emergency lighting.
Gabinetes contra incendio (hidrantes interiores) | 5000 | 8000 | 12000 | 8000 | 2-3 standpipe cabinets per building code.
Subtotal | 56000 | 90000 | 128000 | 90000
7. SECURITY & ACCESS CONTROL
Control de acceso (lectores, torniquetes, software) | 8000 | 12000 | 18000 | 12000 | Biometric/card readers at 8-10 access points + server.
Subtotal | 8000 | 12000 | 18000 | 12000
8. LOADING DOCK & MATERIAL HANDLING
Adecuación de docks (rampas niveladoras, sellos) | 8000 | 15000 | 25000 | 15000 | Shell has docks but may need levelers, seals, bumpers. 2-3 docks.
Señalización industrial interior + exterior | 3000 | 5000 | 8000 | 5000 | Floor markings, 5S, traffic lanes, safety signage.
Subtotal | 11000 | 20000 | 33000 | 20000
9. COMPLIANCE & PERMITS
Licencia de uso de suelo / permisos municipales | 2000 | 4000 | 8000 | 4000 | Municipio depending on location.
Dictamen de Protección Civil | 3000 | 5000 | 8000 | 5000 | Required for industrial operations.
Verificación de instalación eléctrica (UVIE) | 2000 | 3000 | 5000 | 3000 | Mandatory electrical inspection unit per NOM-001-SEDE.
Licencia ambiental / manifiesto de impacto | 2000 | 3000 | 5000 | 3000 | SEMARNAT if applicable. Low impact for assembly.
Ingeniería y proyecto ejecutivo (MEP) | 15000 | 25000 | 35000 | 25000 | Architectural + MEP engineering drawings. Required for permits.
Subtotal | 24000 | 40000 | 61000 | 40000
10. CONTINGENCY
Contingencia (15% del total) | 65700 | 105000 | 149700 | 105000 | FORMULA: 15% of categories 1-9.
Subtotal | 65700 | 105000 | 149700 | 105000
TOTAL FACILITY BUILD-OUT (not in current CAPEX) | 503700 | 805000 | 1147700 | 805000 | Costs NOT in Factory Cost or Funding Structure
Current CAPEX (Production Equipment — Factory Cost) |  |  |  | 885357 | Per Funding Structure. Workstations, tools, test equip, burn-in infra.
TOTAL REVISED CAPEX (Equipment + Facility) | 1389057 | 1690357 | 2033057 | 1690357
IMPACT ON INVESTOR ASK
Current ASK |  |  |  | 5441223 | Per Funding Structure: WC $4.3M + CAPEX $885K + Founders $253K
Additional facility build-out needed | 503700 | 805000 | 1147700 | 805000
REVISED ASK | 5944923 | 6246223 | 6588923 | 6246223 | Recommend rounding to $6M-$6.5M for investor deck
ITEMS REMOVED FROM v1 (per Enrique's feedback 2026-03-23)
✗ Subestación eléctrica 500 kVA — Already included in shell lease (transformer provided)
✗ Acometida CFE + trámite GDMTH — Already in the building, CFE hookup done
✗ Extracción y ventilación industrial — No extractors/louvers (introduces dust). Smoke test extraction in Factory Cost
✗ CCTV (cámaras IP + NVR) — Private industrial park, not Phase 1. Will add from operating cash flow
✗ Cerca perimetral / bardas — Not applicable (private park)
✗ Alarma perimetral + monitoreo — Not applicable (private park)
✗ Racks de almacén (pallet racking) — Already budgeted elsewhere
✗ Montacargas / pallet jack eléctrico — Already budgeted elsewhere

## Benchmarks & References
Industry Benchmarks — Facility Build-Out Costs
COST PER AREA BENCHMARKS
Facility Type | USD/sq ft | USD/m² | Implied Total (5,000 m²) | Source
Basic warehouse shell (Mexico) | $25-40 | $270-430 | $1.35M-$2.15M | NAPS Intl / Cushman & Wakefield 2025
Light manufacturing fit-out (Mexico) | $15-30 | $160-320 | $0.8M-$1.6M | Tetakawi / Co-Production International
Electronics assembly (cleanroom-lite) | $30-60 | $320-645 | $1.6M-$3.2M | Assembly Magazine Capital Survey 2022
Data center build-out (Tier II-III) | $600-1,100 | $6,450-11,830 | $32M-$59M | Dgtl Infra — NOT comparable, reference only
GPW current CAPEX (equipment only) | $16.45 | $177 | $885K | Factory Cost + Funding Structure
GPW revised (equip + facility, mid) |  |  |  | This analysis — see Resumen Ejecutivo
COMPONENT COST BENCHMARKS (Mexico)
Component | Range (MXN/m²) | Range (USD/m²) | For 5,000 m² (USD) | Source
Piso epóxico industrial | $120-300 MXN | $7-17 | $35K-$85K | Cronoshare MX 2025
Piso epóxico ESD-rated | $250-600 MXN | $14-34 | $70K-$170K | 2x-3x standard premium
Remodelación nave (general) | $1,000-7,000 MXN | $56-393 | $280K-$1.96M | Cronoshare MX — depends on scope
Subestación 500 kVA | $800K-1.8M MXN | $45K-101K | N/A — included in shell | MercadoLibre MX + industrial contractors
Sprinklers (wet pipe) | $120-300 MXN/m² | $7-17 | $35K-$85K | Protectamx.com 2024
HVAC industrial (rooftop) | $300-500 MXN/m² | $17-28 | $85K-$140K | MX industrial HVAC contractors
Cableado estructurado (por punto) | $4,500-8,000 MXN/pto | $250-450/drop | $25K-$45K (100 drops) | SC Telecom MX
Iluminación LED industrial | $80-200 MXN/m² | $4.5-11 | $22K-$55K | LED industrial suppliers MX
Oficinas (tablaroca + acabados) | $1,200-2,500 MXN/m² | $67-140 | $54K-$112K (800m²) | Construction cost MX 2025

## Gap Analysis
Gap Analysis — Current CAPEX vs. Real Requirements (v2)
Updated per Enrique's feedback: transformer + CFE in shell, no CCTV/perimeter, racking/forklifts budgeted
Item | In Factory Cost? | In Funding Str.? | Gap (USD) | Status / Notes
--- COVERED (no gap) --- |  |  | —
Workstations (Worksmart 85030) | YES | YES | — | Covered. 22 cells priced.
Cell tools | YES | YES | — | Covered per cell.
Test equipment (smoke, burn-in) | YES | YES | — | Covered.
UPS bank (156 kW) | YES | YES | — | $75K covered.
Generator + ATS (200 kW) | YES | YES | — | $30K covered.
ServerLIFT (shared) | YES | YES | — | Covered.
ESD mats + barcode equip | YES | YES | — | Covered per cell.
Subestación 500 kVA | IN SHELL | N/A | — | Transformer included in lease.
Acometida CFE / GDMTH | IN SHELL | N/A | — | CFE hookup already done.
Pallet racking | ELSEWHERE | ELSEWHERE | — | Already budgeted.
Montacargas/pallet jacks | ELSEWHERE | ELSEWHERE | — | Already budgeted.
--- GAP: NOT BUDGETED --- |  |  | —
Distribution panels (plant-wide) | PARTIAL | PARTIAL | 18000 | Only burn-in panels covered.
Interior electrical distribution | NO | NO | 40000 | 5,000 m² wiring, conduit.
Industrial LED lighting | NO | NO | 28000 | Shell has no lighting.
Grounding + lightning | NO | NO | 8000 | Critical for ESD.
HVAC production (3,000 m²) | NO | NO | 85000 | Cannot assemble without climate control.
HVAC offices (800 m²) | NO | NO | 22000 | Monterrey heat.
Chiller installation (piping, pumps) | PARTIAL | PARTIAL | 40000 | Equipment covered, installation not.
HVAC ductwork | NO | NO | 25000 | Full plant ductwork.
ESD-rated epoxy flooring (prod) | NO | NO | 75000 | CRITICAL. Shell = bare concrete.
Standard epoxy (warehouse) | NO | NO | 21000 | Forklift traffic.
Floor leveling | NO | NO | 15000 | Required before epoxy.
Office construction (800 m²) | NO | NO | 60000 | Shell = no offices.
Training room | NO | NO | 8000 | For 74 HC.
Quality lab | NO | NO | 15000 | OEM quality requirements.
Break room / comedor | NO | NO | 10000 | NOM-001-STPS.
Locker rooms / restrooms | NO | NO | 12000 | Additional for 74 HC.
IT/MES server room | NO | NO | 10000 | Small but critical.
Structured cabling (100+ drops) | NO | NO | 25000 | MES, test, offices.
WiFi infrastructure | NO | NO | 8000 | Industrial APs.
Network switches | NO | NO | 8000 | Core + distribution.
Internet link | NO | NO | 5000 | Fiber + backup.
Sprinkler system (5,000 m²) | NO | NO | 65000 | NFPA 13 required.
Fire detection/alarm | NO | NO | 12000 | Addressable system.
Extinguishers/signage | NO | NO | 5000 | NOM-002-STPS.
Fire cabinets | NO | NO | 8000 | Standpipes.
Access control | NO | NO | 12000 | Card/biometric readers.
Dock adaptation (levelers, seals) | NO | NO | 15000 | Needs levelers/seals.
Floor markings / 5S | NO | NO | 5000 | Safety markings.
Permits / licenses | NO | NO | 12000 | Municipal + Protección Civil.
UVIE electrical verification | NO | NO | 3000 | Mandatory.
Environmental license | NO | NO | 3000 | SEMARNAT.
MEP engineering project | NO | NO | 25000 | Drawings for permits.
TOTAL GAP (Best Estimate) |  |  | 703000 | Before contingency. Add 15% = $808,449